# EN54 FireProtect (VAD) Jeweller

Wireless addressable visual fire alarm device (VAD)

| ### Communication | Jeweller communication technology Proprietary wireless communication technology to transmit commands, alarms, and events. Key features: - Two-way communication. - Advanced sabotage protection. - Block encryption featuring a dynamic key. - Instant notifications. - Remote control and configuration in Ajax apps. Frequency bands 866.0–866.5 MHz 868.0–868.6 MHz 868.7–869.2 MHz 905.0–926.5 MHz 915.85–926.5 MHz 921.0–922.0 MHz Depends on the sales region. Maximum effective radiated power (ERP) up to 20 mW Automatic power control to reduce power consumption and radio interference. Radio signal modulation GFSK Radio communication range up to 1,700 m up to 5,550 ft Between the device and control and indicating equipment (CIE) or a range extender in an open space. Encrypted communication All stored and transmitted data is protected by block encryption featuring a dynamic key. Frequency hopping To prevent radio interference and jamming. |
| --- | --- |
| ### Alarm annunciation | Alarm type light LED frame. Flash frequency 90 ms ON / 1,910 ms OFF (cycle duration: 2,000 ms; frequency: 0.5 Hz) Alarm annunciation test To check the visual alarm signal to ensure fire alarm signals are visible in the premises. |
| ### Installation recommendations | The device's recommended installation height is up to 3 m on the ceiling and up to 2.4 m on the wall. The device's recommended installation height is up to 9.8 ft on the ceiling and up to 7.8 ft on the wall. The device is designed for outdoor and indoor use. |
| ### Sabotage protection | Tamper button Fault notification when an attempt is made to remove the device from the mounting panel. Lock for SmartBracket to secure the device on the SmartBracket mounting panel When locked, the lock secures the device and prevents it from being removed without a special tool. Protection against spoofing device authentication Connection loss detection after 36 s Detection time depends on Jeweller settings. |
| ### Power supply | Battery 4 × CR123A Pre-installed. Tool-free battery replacement To replace the batteries, turn the battery compartment cover counterclockwise. Learn more Reverse polarity protection Prevents device damage if the batteries are put in incorrectly. Recommended battery type Huiderui CR123A; 3 V; 1,600 mAh, LiMnO₂ Calculated battery life up to 5 years |
| ### Enclosure | Dimensions 145 × 145 × 51 mm 5.71" × 5.71" × 2.00" Weight 509 g 1.122 lb Operating temperature range from –10 °C to +50 °C from 14 °F to 122 °F Operating humidity up to 80% Protection class IP54 Flammability rating UL 94 V-0 |
| ### Color | Black White Red |
| ### Complete set | EN54 FireProtect (VAD) Jeweller 4 × CR123A battery (pre-installed) SmartBracket mounting panel Installation kit Quick start guide |
| ### Revision | 1 |
| Warranty | 24 months |